## 400V&large capacity
Items | 400V
| Sinexcel AHF 005/010/015 | Sinexcel AHF 025/035 | Sinexcel AHF 050/060 | Sinexcel AHF 075/100 | Sinexcel AHF 150 | Sinexcel AHF 300
System Parameter
Input phase voltage range | 380 (228V~456V)
Power grid fenquency | 50/60Hz (range: 45Hz~62Hz )
Parallel operation | Unlimited
Overall efficiency | ≥97% (Full load)
Power grid structure | 3P3W/3P4W
CT Ratio | 50/5~10000/5 | 50/5-10000/5 (15A)；150/5~30,000/5 (25~150A) module；600/5~10000/5（300A）
Circuit toplogy | 3-Level
Peroformance Indicator
Rated capacity | 5A/10A/15A | 25A/35A | 50A/60A | 75A/100A | 150A | 300A
Function | Harmonic compensation, Reactive power compensation, Unbalance compensation
Control algorithm | Intelligent FFT/ Instantaneous Reactive Power/FFT
Filtering range | 2nd to 61th orders | 2nd to 50th orders
Filtering performance | ≥95%
Reaction time | 20μs | <50μs
Overall response time | 5ms | <5ms
Target power factor | Adjustable from -1 to +1
Switch frequency | Average 50KHz | Average 20KHz
Cooling air requirement | 96CFM | 321CFM | 321CFM | 543CFM | 825CFM | 1611CFM
Noise level | <68dB | <56dB |  |  | <65 dB | <75dB
Communication & Monitoring Capability
Communications ports | RS485 | RS485, Ethernet port (RJ45)
Commmunications protocols | MODBUS (RTU) | MODBUS (RTU, TCP/IP)
Module display interface | WIFI display, 7-inch HMI(central monitor) | 4.3-inch HMI (module), 7-inch HMI(central monitor), LED
Protection functions | Abnormal voltage/frequency protection; Inverter short-circuit protection; Abnormal output current protection; Inverter over-loaded protection, Over-tempearture protection etc,.
Monitoring alarm | Avaliable
Fault alarm | Avaliable | Available, 500 alarm records
Mechanical Properties
Mounting type | Wall-mounted/Rack-mounted | Wall-mounted/Rack-mounted/Cabinet
Dimensions(W x D x H)mm | 410*340*45(Rack-mounted) 410*45*340(Wall-mounted) | 400*490*150 (Rack-mounted) 440*150*470 (Wall-mounted) | 440*590*190 (Rack-mounted) 440*190*610 (Wall-mounted) | 500*600*190(75A) 440*599*230(100A) (Rack-mounted) 500*190*585(75A) 440*232*625(100A) (Wall-mounted) | 500*560*269 (Rack-mounted) 500*286*557 (Wall-mounted) | 500*722*370 (Rack-mounted) 500*370*722 (Wall-mounted)
Module net weight | 4.98kg | 18kg | 35kg | 40kg | 48kg | 110kg
Color | Silver | Black
Environment Requirement
Attitude | ≤1500m; Between 1500m to 4000m, derating 1% every additional 100m
Ambient temperature | ~10℃~40℃（may derating if ambient temperature exceeds 45℃ )
Relative humidity | 5%~95%, non-condensing
Protection class | IP20 (IP degrees can be customizd)
Related Qualifications & Standards
Qualifications | CE, CCS
Standards compliance | IEEE519, ER G5/4, IEC 61000

## NA&690V
Items | 208V | 480V | 600V | 690V
| Sinexcel AHF 25/35/50/60/75/100 | Sinexcel AHF 25/35/50/60/75/100 | Sinexcel AHF 25/35/50/60/75/100 | Sinexcel AHF 25/35/50/60/75/100
System Parameter
Input phase voltage range | 208V(176V~264V) | 480V(384V-552V) | 600V(420V-690V) | 690V(483V-793V)
Power grid fequency | 50/60Hz (range: 45Hz~62Hz )
Parallel operation | Unlimited | Unlimited
Efficiency | ≥97% | ≥97%
Power grid structure | 3P3W/3P4W | 3P3W/3P4W
CT Ratio | 150/5~30,000/5 | 150/5-10,000/5
Circuit topology | 3-Level | 3-Level
Performance Indicator
Rated capacity | 25/35/50/60/75/100A | 25/35/50/60/75/100A
Function | Harmonic compensation, Reactive power compensation, Unbalance compensation
Control algorithm | FFT/ Intelligent FFT/ Instantaneous Reactive Power
Filtering range | 2nd to 50th orders
Filtering performance | >95%
Reaction time | <50μs
Overall response time | <5ms
Target power factor | Adjustable from -1 to +1
Switching frequency | Average 20KHz
Cooling air requirement | 761CFM | For 25/35/50A 725CFM; For 60/75/100A 761CFM
Noise level | <65dB
Communication & Monitoring Capability
Communication ports | RS485, Ethernet port (RJ45)
Communications protocols | MODBUS (RTU, TCP/IP)
Module display interface | 7-inch LCD touched screen/LED(rack-mounted); 4.3-inch LCD touched screen(wall-mounted)
Protection functions | Abnormal voltage/frequency protection; Inverter short-circuit protection; Abnormal output current protection; Inverter over-loaded protectio; Over-tempearture protection etc,.
Monitoring alarm | Available
Fault alarm | Available, 500 alarm records
Machanical Properties
Mounting type | Wall-mountedd/Rack-mounted/Cabinet
Dimensions (WxDxH)mm | For 25/35/50A 500*540*180 (Rack-mounted) 500*184*627 (Wall-mouned) For 60/75/100A 500*675*250 (Rack-mounted) 500*250*675 (Wall-mouned)
Module net weight | 70kg | 40kg (25/35/50A); 70kg (60/75/100A)
Color | Black
Environment Requirement
Altitude | ≤1500m; Between 1500m to 4000m, derating 1% every additional 100m
Ambient temperature | -20℃-40℃（may derate capacity if ambiet temperature exceeds 45℃）
Relative humidity | 5% to 95%, non-condensing
Protection class | IP20
Related Qualifications & Standards
Qualifications | CE, cULus, DNV/BV/RINA
Standards compliance | IEEE 519, ER G5/4, IEC 61000