## 400V&large capacity
Item | 400V |  |  |  | 480~690V(Large capacity)
| Sinexcel ASVG 030 | Sinexcel ASVG 050 | Sinexcel ASVG 100 | Sinexcel ASVG 200 | Sinexcel ASVG 480 | Sinexcel ASVG 600 | Sinexcel ASVG 690
System Parameter
Rated input line voltage | 400V |  |  |  | 480V | 600V | 690V
Input phase voltage ange | 228V~456V |  |  |  | 384V~576V | 480V~720V | 552V~759V
Power grid frequency | 50Hz/60Hz(range:45Hz~62Hz)
Parallel operation | Unlimited |  |  |  | Unlimited
Overall efficiency | >97% |  |  |  | >99% (at 50% inductive load)
Power grid structure | 3P3W/3P4W |  |  |  | 3P3W
CT | 150/5~30,000/5 |  |  | 600/5~10000/5 | 800/5~10,000/5
Circuit topology | 3-Level
Performance Indicator
Single-module compensation capacity | 30kvar | 50kvar | 100kvar | 200kvar | 480/960/1440/1920/2400kvar | 600/1200/1800/2400/ 3000kvar | 690/1380/2070/2760/3450kvar
Response time | <15ms |  |  |  | <40ms
Target power factor | Adjustable from-1 to+1
Cooling mode | 222L/sec |  | 405L/sec | 500L/sec | Smart air cooling:3000m3/h(*1-4)
Noise level per module | <65dB |  |  | <75dB | <70dB
Communication & Monitoring Capability
Communications ports | RS485,CAN (reserved), Ethernet port (RJ45) |  |  |  | RS485, Ethernet port (RJ45)
Communications portocols | Modbus
Protection functions | Abnormal voltage/frequency protection; Inverter short-circuit protection; Abnormal output current protection; Inverter over-loaded protection, Over-tempearture protection etc,.
Alarm | Available
Monitoring | 4.3-inch touch screen monitor and optional 7-inch touch screen centralized monitor |  |  |  | 7-inch touch screen centralized monitor
Mechanical Properties
Mounting type | Wall-mounted/Rack-mounted/Cabinet |  |  |  | Fixed cabinet
Cable entry mode | Rear entry for rack-mounted type Top entry for wall-mounted type; Top or bottom entry for cabinet |  |  |  | Bottom entry
Dimensions(W x D x H)(mm3) | 500*560*190 (Rack-mounted) 500*191*585 (Wall-mounted) |  | 500x520x269 (Rack-mounted) 500x286x557 (Wall-mounted) | 500*690*370 (Rack-mounted) 500*370*690 (Wall-mounted) | 600*800*2200/1200*800*2200/1800*800*2200/2400*800*2200/3000*800*2200
Module net weight | 36kg |  | 48kg | 110kg | 500kg(one cabinet)
Color | RAL7035(gray)
Environment Requirement
Altitude | ≤1500m; Between 1500m to 4000m, derating 1% every additional 100m.
Ambient temperature | -10℃~40℃(may derate capacity if ambient temperature exceeds 45℃)
Relative humidity | 5%~95%,non-condensing
protection grade | IP20(other IP degrees are customizable)
Related Qualifications & Standards
Qualifications | CE, cETLus |  |  |  | CE

## NA&690V
Item | 208V | 480V | 600V | 690V
| Sinexcel ASVG 35 | Sinexcel ASVG 30/40/50/80 | Sinexcel ASVG 40/50/80/100 | Sinexcel ASVG 40/50/80/120
System Parameter
Input phase voltage range | 208V(176V~264V) | 384V~552V | 420V~690V | 483V~793V
Power grid frequency | 50Hz/60Hz(range:45Hz~66Hz)
Parallel operation | Unlimited
Overall effciency | ≥97%
Power grid structure | 3P3W/3P4W
CT | 150/5~30,000/5
Circute topology | 3-Level
Performance Indicator
Single-module compensation capacity | 35kvar | 30/40/50/80kvar | 40/50/80/100kvar | 40/50/80/120kvar
Function | Reactive power compensation, Three phase balancing, Voltage regulation
Response time | <15ms
Target power factor | Adjustable from-1 to+1
Cooling mode | 761CFM | 725CFM(30/40kvar) 761CFM(50/80kvar) | 725CFM (40/50kvar) 761CFM (80/100kvar) | 725CFM (40/50kvar) 761CFM (80/120kvar)
Noise level per module | <65dB
Communication & Monitoring Capability
Communications ports | RS485, CAN(reserved), Ethernet port(RJ45)
Communications protocols | Modbus
Protection functions | Abnormal voltage/frequency protection; Inverter short-circuit protection; Abnormal output current protection; Inverter over-loaded protection; Over-tempearture protection etc,.
Alarm | Available
Monitoring | 7-inch touch screen centralized monitor(rack-mount) and 4.3-inch touch screen monitor(wall-mount)
Mechanical Properties
Mounting type | Wall-mounted/Rack-mounted/Cabinet
Cable entry mode | Top and bottom entry for cabinet
Dimensions (W×D×H)(mm³) | 500*675*250 (Rack-mounted) 500*250*723 (Wall-mounted) | For 30/40kvar 500*540*180 (Rack-mounted) 500*184*627 (Wall-mouned) For 50/80kvar 500*675*250 (Rack-mounted) 500*250*723 (Wall-mounted） | For 40/50kvar 500*540*180 (Rack-mounted) 500*184*627 (Wall-mouned) For 80/100kvar 500*675*250 (Rack-mounted) 500*250*723 (Wall-mounted） | For 40/50kvar 500*540*180 (Rack-mounted) 500*184*627 (Wall-mouned) For 80/120kvar 500*675*250 (Rack-mounted) 500*250*723 (Wall-mounted）
Module net weight | 70kg | 40kg(30/40kvar) 70kg(50/80kvar) | 40kg(40/50kvar) 70kg(80/100kvar) | 40kg(40/50kvar) 70kg(80/120kvar)
Color | Wall mounted: RAL7035(gray), Rack mounted: original color of aluminum-zinc
Environment Requirement
Altitude | ≤1500m; Between 1500m to 4000m, derating 1% every additional 100m
Ambient temperature | -20℃~40℃(may derate capacity if ambient temperature exceeds 45℃)
Relative temperature | 5%~95%, non-condensing
Protection grade | IP20(other IP degrees are customizable）
Related Qualifications & Standards
Qualifications | CE, cETLus, cULus